## J1
BQDM - Bridge Quench Detection Module Connections
BQDMJ1 |  |  | Connector type: DIN-H 15 pin
Pin | Name | Description | Connected to:
4
6 | TIN | Toroid out - positive voltage input
8
10
12 | TCOM | Toroid common
14
16
18 | TCOM | Toroid common
20
22
24 | TOUT | Toroid out - negative voltage input
26
28
30 | CTM+ | Cable Trace machine, positive side
32 | CTM- | Cable Trace machine, negative side

## J2
BQDM100 - Bridge Quench Detection Module 100 Connections
BQDMJ2 | [5 empty] | Connector type: DIN-C 96-pin
a |  |  |  | b |  |  |  | c
Pin | Name | Description | Connected to: | Pin | Name | Description | Connected to: | Pin | Name | Description | Connected to:
1 | PLCV24IN | 24 V opto power from PLC | PLCCON1-2 | 1 | PLCV24OUT | 24 V relay power to PLC | PLCCON3-4 | 1
2 | PLCGND | Relay ground from PLC | PLCCON5-6 | 2 | MTESTEN | Module Test Enable, from test PLC | PLCCON7-18 | 2 | ANNTINC | TIN Opto-output to Annunc, coll.
3 | MTEST | Module being tested, to PLC | PLCCON19-30 | 3 |  |  |  | 3 | ANNTINE | TIN Opto-output to Annunc, emitt.
4 | ILOOPOUT | Current loop , out |  | 4 | MSSVOUT | Voltage output to MSS, signal |  | 4
5 | ILOOPIN | Current loop, in |  | 5 | MSSVCOM | Voltage output to MSS, common |  | 5 | ANNTOUTC | TOUT Opto-output to Annunc, coll.
6 |  |  |  | 6 |  |  |  | 6 | ANNTOUTE | TOUT Opto-output to Annunc, emitt.
7 |  |  |  | 7 |  |  |  | 7
8 | HWLTINC | TIN Opto-output to HWL, coll. |  | 8 | HWLTOUTC | TOUT Opto-output to HWL, coll. |  | 8
9 | HWLTINE | TIN Opto-output to HWL, emitt. |  | 9 | HWLTOUTE | TOUT Opto-output to HWL, emitt. |  | 9
10 |  |  |  | 10 |  |  |  | 10
11 |  |  |  | 11 |  |  |  | 11
12 |  |  |  | 12 |  |  |  | 12
13 |  |  |  | 13 |  |  |  | 13
14 | INTI0OUT | I=0 interlock, from Magnet Control |  | 14 | PLCTTIN | Test Toroid In, from PLC | PLCC31 | 14 | ANTESTSIG | Analog test signal, from PLC | PLCC33
15 | INTI0IN | I=0 interlock, from Magnet Control |  | 15 | PLCTTOUT | Test Toroid Out, from PLC | PLCC32 | 15 | ANTESTCOM | Analog test common INGDA1 | PLCC34
16 |  |  |  | 16 |  |  |  | 16
17 | PLCVTRIN | Voltage transition, to PLC | PLCC35 | 17 | PLCQIN | Quench detection In, to PLC | PLCC37 | 17 | PLCVOUT | Voltage output to PLC, signal | PLCC39
18 | PLCVTROUT | Voltage transition, to PLC | PLCC36 | 18 | PLCQOUT | Quench detection Out, to PLC | PLCC38 | 18 | PLCVCOM | Voltage output to PLC, common | PLCC40
19 |  |  |  | 19 |  |  |  | 19 | RESOUT | Power out for RESET signal | PLCC41
20 |  |  |  | 20 |  |  |  | 20 | RESIN | Power in for RESET signal | PLCC42
21 |  |  |  | 21 |  |  |  | 21
22 | MFB+ | Module Fault, positive side |  | 22 | CTB+ | Cable Trace, positive side |  | 22
23 | MFB- | Module Fault, negative side |  | 23 | CTB- | Cable Trace, negative side |  | 23
24 | U1 | +5 VDC Isolated supply |  | 24 | U1 | +5 VDC Isolated supply |  | 24 | U1 | +5 VDC Isolated supply
25 | GNDD1 | +5 VDC Isolated ground |  | 25 | GNDD1 | +5 VDC Isolated ground |  | 25 | GNDD1 | +5 VDC Isolated ground
26 | U2 | +24 VDC Isolated supply |  | 26 | U2 | +24 VDC Isolated supply |  | 26 | U2 | +24 VDC Isolated supply
27 | GNDD2 | +24 VDC Isolated ground |  | 27 | GNDD2 | +24 VDC Isolated ground |  | 27 | GNDD2 | +24 VDC Isolated ground
28 | U3 | +15 VDC Positive analog supply |  | 28 | U3 | +15 VDC Positive analog supply |  | 28 | U3 | +15 VDC Positive analog supply
29 | U4 | -15 VDC Negative analog supply |  | 29 | U4 | -15 VDC Negative analog supply |  | 29 | U4 | -15 VDC Negative analog supply
30 | GNDA | Analog ground |  | 30 | GNDA | Analog ground |  | 30 | GNDA | Analog ground
31 | U5 | +5 VDC Digital supply |  | 31 | U5 | +5 VDC Digital supply |  | 31 | U5 | +5 VDC Digital supply
32 | GNDD | Digital ground |  | 32 | GNDD | Digital ground |  | 32 | GNDD | Digital ground