QUENCH DETECTOR REQUIREMENTS FOR RAL

I found that due to my inability to understand the French language, that I could not follow several of the discussions during the meeting at Saclay.  As such I would like to re state RAL’s basic requirements for their quench detector system.

The Quench detector should be of simple design, its basic function being to detect the  start of a quench. This resulting information must be sent to the hardwired interlock system, a monitoring plc and annunciator equipment by way of volt free relay contacts . The relays must be configured in the normal fail safe fashion.

RAL require a dual redundant system comprising of two totally independent systems, each system will monitor 6 channels (3 per end cap toroid).

GENERAL PRINCIPLE

RAL will require an asymmetric bridge system to monitor the two sets of three voltage taps within each end cap. The voltage on each tap will be compared with a given fraction of the associated overall toroid’s voltage, any significant differential voltage between which will be indicative of a quench. A potentiometer system will be provided to enable each bridge to be independently tuned.

The differential voltages produced within the bridge circuits will be rectified and filtered before the processed signals are sent to comparator circuits.

The comparator circuits will compare the magnitude of each processed signal against the magnitude of an adjustable trip level. If a given signal’s magnitude exceeds the magnitude of the trip level an adjustable timing circuit will be initiated. Only when a processed signal’s magnitude constantly exceeds the trip level for the duration set by the timing circuit will a real quench be deemed to be occurring and the associated output relay be de-energised.

Each channel will control an independent relay, contacts of which will be used within the hardwired interlock circuitry, a monitoring plc and the annunciator equipment. Each relay must be energised when the associated channel is deemed to be healthy.

LOCAL INDICATION

RAL will require a local indication LED for each channel. The LED’s will simply state the health status of each channel and can typically be driven by the channel’s associated output relay. RAL do not want local latched or first up indication of the detector channels, such information is provided by the annunciator circuitry.

TESTING

RAL’s requirements for testing consist of a simple test box which will inject a variable offset voltage into the bridge circuitry. The signals from this test box will typically be connected to the quench circuitry via the connectors which are normally used for the voltage taps. This scheme is already being used in previous detectors, tests of this nature are generally carried out on a yearly basis.

Automatic testing is not a RAL requirement. If such a scheme is to be used it must not reduce the reliability of the basic quench detector function, it must be removable from the quench detector circuit if so desired and must be interlocked to prevent testing while the toroids are energised.

CONNECTORS

A system is required to prevent the toroids being energised until all connectors are mated correctly, this will be achieved by mechanically polarised connectors and electrical trace circuits. An interlock will prevent energisation until all trace circuits are complete a subsequent breakage in the trace circuit will result in a dumping action. The detector system must incorporate the above facilities.